## README
REACTIVE POWER COMPENSATION SIZING TOOL
A standalone Excel version of the reactive power sizing app. Sheets:
1. Sizing — the calculation chain: grid demand, transformer consumption, losses, inverter sizing, checks.
2. GridCodes — database of published grid-code reactive requirements; pick one from the dropdown (B1).
3. InverterPQ — the manufacturer's Q(t)-mode capability table (% of rated kVA per voltage and loading).
4. Compliance — V-Q at Registered Capacity and P-Q at nominal voltage vs the selected grid code, with charts.
Colour key: yellow = input cells, grey = calculated, green = key results.
Notes:
- Inverter count: leave the manual-count cell blank to auto-size (meets both reactive and delivery needs).
- Reactive capability precedence: capability table (if 'Use table' = Yes) > manual kVAr override > sqrt(S²-P²).
- Compliance dispatches inverters at (grid limit + losses) / count, as in a G99 Type C study.
- Export capability is net of transformer consumption; absorption is aided by it; capacitor bank exports only.
- Voltage capability is interpolated linearly between the capability-table rows (conservative across N/A gaps).
- Grid-code presets are typical published values — always confirm against your interconnection agreement.
- This tool is an analytic screening aid, not a substitute for a network load-flow study.

## Sizing
SIZING
PROJECT
Project name | Belvior
STEP 1 — INITIAL SIZING
Grid injection limit / Registered Capacity | 52.8 | MW
Power factor at grid | 0.95 | cos φ
MVA rating of plant |  | MVA
MVAr demand (grid PF) |  | MVAr
STEP 2 — TRANSFORMER REACTIVE CONSUMPTION
Group | Qty | kVA | Z % | Q (kVAr)
TS Block 1 | 3 | 10164 | 9.5
TS Block 2 | 4 | 7260 | 9.5
Auxiliary transformer (MCR) | 1 | 500 | 4.5
Design margin on transformer demand | 10 | %
Transformer demand incl. margin |  | MVAr
TOTAL REACTIVE DEMAND |  | MVAr
STEP 3 — INTERNAL SYSTEM LOSSES
Loss source | Fraction % | Loss (MW)
AC cable loss | 1
Auxiliary system loss (string inverters) | 1
Transmission line loss | 0.3
Miscellaneous losses | 1
Total system losses |  | MW
Capacity to be considered |  | MW
STEP 4 — INVERTER CAPABILITY & COMPENSATION
Inverter apparent power | 363 | kVA
PF at inverter level (tip: Goal Seek on B47/B48) | 0.918 | cos φ
Active power / inverter |  | kW
Reactive capability — derived √(S²-P²) |  | kVAr
Reactive capability — manual override (optional) |  | kVAr
Reactive capability — from InverterPQ table |  | kVAr
Q per inverter USED |  | kVAr
Capacitor bank | 0 | MVAr
Q for inverters (after cap bank) |  | MVAr
Manual inverter count (blank = auto) |  | nos.
Required inverters — reactive |  | nos.
Required inverters — active delivery |  | nos.
INVERTERS IN DESIGN |  | nos.
Power delivered to grid (net of losses) |  | MW
Reactive power compensated |  | MVAr
Delivery check (≥ grid limit)
Reactive check (≥ total demand)

## GridCodes
GRID CODE REQUIREMENT DATABASE
Selected grid code: | United Kingdom - ENA G99 / GB Grid Code (Type C/D PPM)
Key | Name | Q/Pmax | PF | pMin % | pFullLag % | Relief | Stub | VFullLo | VFullHi | Asym | VZeroLo | VZeroHi | Notes
gb_g99 | United Kingdom - ENA G99 / GB Grid Code (Type C/D PPM) | 0.329 | 0.95 | 20 | 20 | 1 | 0.05 | 0.95 | 1.05 | 1 | 0.9 | 1.1 | 0.95 lead/lag at RC from 20% output (G99 13.5.5, Fig 13.13/13.14). Asymmetric V-Q; lead relief triangle 20-50% at DNO discretion; ±5% band below 20%.
de_4110 | Germany - VDE-AR-N 4110 (medium voltage) | 0.329 | 0.95 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.925 | 1.075 | cos φ 0.95 under/overexcited above 20% of installed capacity; control range 0.925-1.075 pu.
de_4120 | Germany - VDE-AR-N 4120 (high voltage) | 0.411 | 0.925 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | cos φ 0.925 variant (three TSO-selectable variants exist).
us_1547b | USA - IEEE 1547-2018 (Category B) | 0.44 | 0.9 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Inject/absorb 44% of nameplate kVA (~0.90 PF at rated); full capability above 20% of rated power.
au_ner | Australia - NER S5.2.5.1 (Automatic access) | 0.395 | 0.93 | 0 | 0 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | ±0.395 x rated active power at any output level.
eu_rfg | EU - ENTSO-E RfG (typical Type C/D implementation) | 0.329 | 0.95 | 20 | 50 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Regulation 2016/631 leaves envelopes to each TSO - typical national choice shown.
pf95 | Generic - fixed PF 0.95 lead/lag | 0.329 | 0.95 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Fixed PF, full Q above 20% output.
pf90 | Generic - fixed PF 0.90 lead/lag | 0.484 | 0.9 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Fixed PF, full Q above 20% output.
Active parameters (looked up from the selected code):
| Q/Pmax | PF | pMin % | pFullLag % | Relief | Stub | VFullLo | VFullHi | Asym | VZeroLo | VZeroHi

## InverterPQ
INVERTER P-Q CAPABILITY TABLE
Use capability table for sizing? | Yes
Max reactive power, % of rated kVA. Blank = N/A (operation not permitted). Rows ascending in voltage.
V (pu) \ P (pu) | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0.85 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 48.2 | 28.7
0.9 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 56.6 | 41.2 | 0
0.95 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 51.2 | 30.4
1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 43.6 | 0
1.05 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 43.6 | 0
1.1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 43.6 | 0
Sizing lookup (1.00 Vn row at PF loading):
Loading (= inverter PF) | bar: 0
q% at 1.00 Vn | bar: 0
q (kVAr) at 1.00 Vn | bar: 0

## Compliance
GRID CODE COMPLIANCE
OPERATING POINT (Registered Capacity dispatch)
Dispatch / inverter | [8 empty] | kW
Dispatch loading | [8 empty] | pu
Qmax required | [8 empty] | MVAr
CAPABILITY AT TABLE VOLTAGES (per-inverter q% at dispatch loading)
V (pu) | q%/inv | [10 empty] | Req polygon Q | V
V-Q AT REGISTERED CAPACITY — interpolated sweep and A/B/E/F corner points
Point | V (pu) | j | VA | VB | qA | qB | t | q%/inv | Q prod (MVAr) | Q abs (MVAr) | Req lag (MVAr) | Req lead (MVAr) | -Q abs | Status
0.85
0.8625
0.875
0.8875
0.9
0.9125
0.925
0.9375
0.95
0.9625
0.975
0.9875
1
1.0125
1.025
1.0375
1.05
1.0625
1.075
1.0875
1.1
A
B
E
F
P-Q AT NOMINAL VOLTAGE (1.00 pu)
P (pu) | P (MW) | disp kW | loading |  |  |  |  | q%/inv | Q prod (MVAr) | Q abs (MVAr) | Req lag (MVAr) | Req lead (MVAr) | -Q abs | Status | -Req lead
0
0.025
0.05
0.075
0.1
0.125
0.15
0.175
0.2
0.225
0.25
0.275
0.3
0.325
0.35
0.375
0.4
0.425
0.45
0.475
0.5
0.525
0.55
0.575
0.6
0.625
0.65
0.675
0.7
0.725
0.75
0.775
0.8
0.825
0.85
0.875
0.9
0.925
0.95
0.975
1
MSOL
OVERALL VERDICT