## README
REACTIVE POWER COMPENSATION SIZING TOOL
A standalone Excel version of the reactive power sizing app. Sheets:
1. Sizing — the calculation chain: grid demand, transformer consumption, losses, inverter sizing, checks.
2. GridCodes — database of published grid-code reactive requirements; pick one from the dropdown.
3. InverterPQ — the manufacturer's Q(t)-mode capability table (%% of rated kVA per voltage row and loading).
4. Compliance — V-Q at Registered Capacity and P-Q at nominal voltage vs the selected grid code, with charts.
Colour key: yellow = input cells, grey = calculated, green = key results.
Notes:
- Inverter count: leave the manual-count cell blank to auto-size (meets both reactive and delivery needs).
- Reactive capability precedence: capability table (if 'Use table' = Yes) > manual kVAr override > sqrt(S^2-P^2).
- Compliance dispatches inverters at (grid limit + losses) / count, as in a G99 Type C study.
- Export capability is net of transformer consumption; absorption is aided by it; capacitor bank exports only.
- Grid-code presets are typical published values - always confirm against your interconnection agreement.
- This tool is an analytic screening aid, not a substitute for a network load-flow study.

## Sizing
PROJECT
Project name | Belvior
STEP 1 — INITIAL SIZING
Grid injection limit / Registered Capacity | 52.8 | MW
Power factor at grid | 0.95 | cos phi
MVA rating of plant | 55.5789 | MVA
MVAr demand (grid PF) | 17.3545 | MVAr
STEP 2 — TRANSFORMER REACTIVE CONSUMPTION
Group | Qty | Rating (kVA) | Impedance (%) | Q (kVAr)
TS Block 1 | 3 | 10164 | 9.5 | 2896.74
TS Block 2 | 4 | 7260 | 9.5 | 2758.8
Auxiliary transformer (MCR) | 1 | 500 | 4.5 | 22.5
0
0
0
Design margin on transformer demand | 10 | %
Transformer demand incl. margin | 6.2458 | MVAr
TOTAL REACTIVE DEMAND | 23.6004 | MVAr
STEP 3 — INTERNAL SYSTEM LOSSES
Loss source | Fraction (%) | Loss (MW)
AC cable loss | 1 | 0.528
Auxiliary system loss (string inverters) | 1 | 0.528
Transmission line loss | 0.3 | 0.1584
Miscellaneous losses | 1 | 0.528
Total system losses | 1.7424 | MW
Capacity to be considered | 54.5424 | MW
STEP 4 — INVERTER CAPABILITY & COMPENSATION
Inverter apparent power | 363 | kVA
PF at inverter level (use Data > What-If > Goal Seek on B45 or B46) | 0.918 | cos phi
Active power / inverter | 333.234 | kW
Reactive capability - derived sqrt(S^2-P^2) | 143.9587 | kVAr
Reactive capability - manual override (optional) |  | kVAr
Reactive capability - from InverterPQ table (at PF loading) | 129.7798 | kVAr
Q per inverter USED | 129.7798 | kVAr
Capacitor bank | 0 | MVAr
Q for inverters (after cap bank) | 23.6004 | MVAr
Manual inverter count (blank = auto) |  | nos.
Required inverters - reactive | 182 | nos.
Required inverters - active delivery | 164 | nos.
Inverters in design | 182 | nos.
Power delivered to grid (net of losses) | 58.9062 | MW
Reactive power compensated | 23.6199 | MVAr
Delivery check (>= grid limit) | PASS
Reactive check (>= total demand) | PASS

## GridCodes
Selected grid code: | United Kingdom - ENA G99 / GB Grid Code (Type C/D PPM)
Key | Name | Q/Pmax | PF | pMin % | pFullLag % | Relief | Stub | VFullLo | VFullHi | Asym | VZeroLo | VZeroHi | Notes
gb_g99 | United Kingdom - ENA G99 / GB Grid Code (Type C/D PPM) | 0.329 | 0.95 | 20 | 20 | 1 | 0.05 | 0.95 | 1.05 | 1 | 0.9 | 1.1 | 0.95 lead/lag at RC from 20% output (G99 13.5.5, Fig 13.13/13.14). Asymmetric V-Q; lead relief triangle 20-50% at DNO discretion; +/-5% band below 20%.
de_4110 | Germany - VDE-AR-N 4110 (medium voltage) | 0.329 | 0.95 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.925 | 1.075 | cos phi 0.95 under/overexcited above 20% of installed capacity; control range 0.925-1.075 pu.
de_4120 | Germany - VDE-AR-N 4120 (high voltage) | 0.411 | 0.925 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | cos phi 0.925 variant (three TSO-selectable variants exist).
us_1547b | USA - IEEE 1547-2018 (Category B) | 0.44 | 0.9 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Inject/absorb 44% of nameplate kVA (~0.90 PF at rated); full capability above 20% of rated power.
au_ner | Australia - NER S5.2.5.1 (Automatic access) | 0.395 | 0.93 | 0 | 0 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | +/-0.395 x rated active power at any output level.
eu_rfg | EU - ENTSO-E RfG (typical Type C/D implementation) | 0.329 | 0.95 | 20 | 50 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Regulation 2016/631 leaves envelopes to each TSO - typical national choice shown.
pf95 | Generic - fixed PF 0.95 lead/lag | 0.329 | 0.95 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Fixed PF, full Q above 20% output.
pf90 | Generic - fixed PF 0.90 lead/lag | 0.484 | 0.9 | 20 | 20 | 0 | 0 | 0.95 | 1.05 | 0 | 0.9 | 1.1 | Fixed PF, full Q above 20% output.
Active parameters (looked up from the selected code):
| Q/Pmax | PF | pMin % | pFullLag % | Relief | Stub | VFullLo | VFullHi | Asym | VZeroLo | VZeroHi
| 0.329 | 0.95 | 20 | 20 | 1 | 0.05 | 0.95 | 1.05 | 1 | 0.9 | 1.1

## InverterPQ
Use capability table for sizing? | Yes
Max reactive power, % of rated kVA (blank = N/A, operation not permitted)
V (pu) \ P loading (pu) | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
1.1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 43.6 | 0
1.05 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 43.6 | 0
1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 43.6 | 0
0.95 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 51.2 | 30.4
0.9 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 56.6 | 41.2 | 0
0.85 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 48.2 | 28.7
Sizing lookup (1.00 Vn row at PF loading):
Loading (= inverter PF) | 0: 0.918
q% at 1.00 Vn | 0: 35.752
q (kVAr) at 1.00 Vn | 0: 129.7798

## Compliance
COMPLIANCE VS SELECTED GRID CODE
Dispatch/inverter | 299.6835 | kW
Dispatch loading | 0.82557 | pu
Qmax required | 17.3712 | MVAr
V-Q AT REGISTERED CAPACITY (table voltages)
V (pu) | q%/inv | Q prod (MVAr) | Q abs (MVAr) | Req lag | Req lead | Status |  | Req polygon |  |  |  | -Q abs (VQ)
1.1 | 55.8058 | 30.6228 | 43.1145 | 0 | 0 | PASS |  | Q | V |  |  | -43.1145
1.05 | 55.8058 | 30.6228 | 43.1145 | 0 | 17.3712 | PASS |  | 0 | 0.95 |  |  | -43.1145
1 | 55.8058 | 30.6228 | 43.1145 | 17.3712 | 17.3712 | PASS |  | 17.3712 | 0.95 |  |  | -43.1145
0.95 | 45.8805 | 24.0656 | 36.5573 | 17.3712 | 0 | PASS |  | 17.3712 | 1 |  |  | -36.5573
0.9 | 30.6633 | 14.0122 | 26.5039 | 0 | 0 | PASS |  | 0 | 1.05 |  |  | -26.5039
0.85 | 0 | -6.2458 | 6.2458 | 0 | 0 | PASS |  | -17.3712 | 1.05 |  |  | -6.2458
[8 empty] | -17.3712 | 1
[8 empty] | 0 | 0.95
P-Q AT NOMINAL VOLTAGE (1.00 pu)
P (pu) | P (MW) | disp (kW) | loading | q%/inv | Q prod | Q abs | Req lag | Req lead | Status | -Req lead | -Q abs
0 | 0 | 0 | 0 | 60 | 33.3938 | 45.8854 | 0 | 0 | PASS | 0 | -45.8854
0.05 | 2.64 | 14.9842 | 0.041279 | 60 | 33.3938 | 45.8854 | 0 | 0 | PASS | 0 | -45.8854
0.1 | 5.28 | 29.9684 | 0.082557 | 60 | 33.3938 | 45.8854 | 0 | 0 | PASS | 0 | -45.8854
0.15 | 7.92 | 44.9525 | 0.12384 | 60 | 33.3938 | 45.8854 | 0 | 0 | PASS | 0 | -45.8854
0.2 | 10.56 | 59.9367 | 0.16511 | 60 | 33.3938 | 45.8854 | 17.3712 | 6.3168 | PASS | -6.3168 | -45.8854
0.25 | 13.2 | 74.9209 | 0.20639 | 60 | 33.3938 | 45.8854 | 17.3712 | 8.1592 | PASS | -8.1592 | -45.8854
0.3 | 15.84 | 89.9051 | 0.24767 | 60 | 33.3938 | 45.8854 | 17.3712 | 10.0016 | PASS | -10.0016 | -45.8854
0.35 | 18.48 | 104.8892 | 0.28895 | 60 | 33.3938 | 45.8854 | 17.3712 | 11.844 | PASS | -11.844 | -45.8854
0.4 | 21.12 | 119.8734 | 0.33023 | 60 | 33.3938 | 45.8854 | 17.3712 | 13.6864 | PASS | -13.6864 | -45.8854
0.45 | 23.76 | 134.8576 | 0.37151 | 60 | 33.3938 | 45.8854 | 17.3712 | 15.5288 | PASS | -15.5288 | -45.8854
0.5 | 26.4 | 149.8418 | 0.41279 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.55 | 29.04 | 164.8259 | 0.45407 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.6 | 31.68 | 179.8101 | 0.49534 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.65 | 34.32 | 194.7943 | 0.53662 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.7 | 36.96 | 209.7785 | 0.5779 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.75 | 39.6 | 224.7626 | 0.61918 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.8 | 42.24 | 239.7468 | 0.66046 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.85 | 44.88 | 254.731 | 0.70174 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.9 | 47.52 | 269.7152 | 0.74302 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
0.95 | 50.16 | 284.6993 | 0.7843 | 60 | 33.3938 | 45.8854 | 17.3712 | 17.3712 | PASS | -17.3712 | -45.8854
1 | 52.8 | 299.6835 | 0.82557 | 55.8058 | 30.6228 | 43.1145 | 17.3712 | 17.3712 | PASS | -17.3712 | -43.1145
OVERALL VERDICT | COMPLIANT